## Sheet1
Input | Peak Usage (gph) | 160
Output | Supply Target Water Temp (°F) | 140
| Incoming Supply Water Temp (°F) | 85
| Existing Storage (gallon) | 300
| Hot Water Usage per day (gallon/day) | 1000
| Peak Energy Req. (BTU/hr) | 73392
| Percentage of water to be used from tank to meet peak demand | 33 | % | (<------- Use 33% if peak usage duration is 3 hr, Use 50% if peak usage duration is 2 hr, Use 75% if peak usage duration is 1 hr)
| Percentage of water reserved in tank | 67 | %
Note:
| Heat Pump Sizing |  |  | Storage + Heat Pump recovery = Water available to meet peak demand
| Energy To be supplied by heat pump alone | 27980.7
| Heat Pump | Heat pump alone satisfies requirement
| C25 | NO
| C60 | YES
| C90 | YES
| C125 | YES
| C185 | YES
| C250 | YES
C25
| Air Condition(°F) |  | 40 | 50 | 60 | 70 | 80 | 90
| Existing Storage ( gallon) |  | 300 | 300 | 300 | 300 | 300 | 300
| Heating Capacity Needed (BTU/hr) |  | 27980.7 | 27980.7 | 27980.7 | 27980.7 | 27980.7 | 27980.7
| Heating Capacity |  | 17000 | 19700 | 22600 | 26000 | 29500 | 33700
| # of C25 needed to meet peak demand |  | 1.6459 | 1.4203 | 1.2381 | 1.0762 | 0.9485 | 0.83029
| Recovery From heatpump (During first hour) |  | 61 | 61 | 61 | 61 | 61 | 61
| Amount of water used from Storage Tank to meet peak usage (During first hour) |  | 99 | 99 | 99 | 99 | 99 | 99
| Peak demand met |  | 160 | 160 | 160 | 160 | 160 | 160
C60
| Air Condition(°F) |  | 40 | 50 | 60 | 70 | 80 | 90
| Existing Storage ( gallon) |  | 300 | 300 | 300 | 300 | 300 | 300
| Heating Capacity Needed (BTU/hr) |  | 27980.7 | 27980.7 | 27980.7 | 27980.7 | 27980.7 | 27980.7
| Heating Capacity |  | 39500 | 45700 | 52400 | 60700 | 68700 | 74700
| # of C60 needed to meet peak demand |  | 0.70837 | 0.61227 | 0.53398 | 0.46097 | 0.40729 | 0.37457
| Recovery From heatpump (During first hour) |  | 61 | 61 | 61 | 61 | 61 | 61
| Amount of water used from Storage Tank to meet peak usage (During first hour) |  | 99 | 99 | 99 | 99 | 99 | 99
| Peak demand met |  | 160 | 160 | 160 | 160 | 160 | 160
C90
| Air Condition(°F) |  | 40 | 50 | 60 | 70 | 80 | 90
| Existing Storage ( gallon) |  | 300 | 300 | 300 | 300 | 300 | 300
| Heating Capacity Needed (BTU/hr) |  | 27980.7 | 27980.7 | 27980.7 | 27980.7 | 27980.7 | 27980.7
| Heating Capacity |  | 68720 | 77980 | 91560 | 103360 | 119870 | 137300
| # of C90 needed to meet peak demand |  | 0.40717 | 0.35882 | 0.3056 | 0.27071 | 0.23343 | 0.20379
| Recovery From heatpump (During first hour) |  | 61 | 61 | 61 | 61 | 61 | 61
| Amount of water used from Storage Tank to meet peak usage (During first hour) |  | 99 | 99 | 99 | 99 | 99 | 99
| Peak demand met |  | 160 | 160 | 160 | 160 | 160 | 160
C125
| Air Condition(°F) |  | 40 | 50 | 60 | 70 | 80 | 90
| Existing Storage ( gallon) |  | 300 | 300 | 300 | 300 | 300 | 300
| Heating Capacity Needed (BTU/hr) |  | 27980.7 | 27980.7 | 27980.7 | 27980.7 | 27980.7 | 27980.7
| Heating Capacity |  | 89100 | 102700 | 117300 | 135100 | 155200 | 169500
| # of C125 needed to meet peak demand |  | 0.31404 | 0.27245 | 0.23854 | 0.20711 | 0.18029 | 0.16508
| Recovery From heatpump (During first hour) |  | 61 | 61 | 61 | 61 | 61 | 61
| Amount of water used from Storage Tank to meet peak usage (During first hour) |  | 99 | 99 | 99 | 99 | 99 | 99
| Peak demand met |  | 160 | 160 | 160 | 160 | 160 | 160
C185
| Air Condition(°F) |  | 40 | 50 | 60 | 70 | 80 | 90
| Existing Storage ( gallon) |  | 300 | 300 | 300 | 300 | 300 | 300
| Heating Capacity Needed (BTU/hr) |  | 27980.7 | 27980.7 | 27980.7 | 27980.7 | 27980.7 | 27980.7
| Heating Capacity |  | 139000 | 160000 | 182000 | 208800 | 240600 | 251500
| # of C185 needed to meet peak demand |  | 0.2013 | 0.17488 | 0.15374 | 0.13401 | 0.1163 | 0.11126
| Recovery From heatpump (During first hour) |  | 61 | 61 | 61 | 61 | 61 | 61
| Amount of water used from Storage Tank to meet peak usage (During first hour) |  | 99 | 99 | 99 | 99 | 99 | 99
| Peak demand met |  | 160 | 160 | 160 | 160 | 160 | 160
C250
| Air Condition(°F) |  | 40 | 50 | 60 | 70 | 80 | 90
| Existing Storage ( gallon) |  | 300 | 300 | 300 | 300 | 300 | 300
| Heating Capacity Needed (BTU/hr) |  | 27980.7 | 27980.7 | 27980.7 | 27980.7 | 27980.7 | 27980.7
| Heating Capacity of Unit |  | 157000 | 188600 | 223100 | 265400 | 310500 | 315400
| # of C250 needed to meet peak demand |  | 0.17822 | 0.14836 | 0.12542 | 0.10543 | 0.090115 | 0.088715
| Recovery From heatpump (During first hour) |  | 61 | 61 | 61 | 61 | 61 | 61
| Amount of water used from Storage Tank to meet peak usage (During first hour) |  | 99 | 99 | 99 | 99 | 99 | 99
| Peak demand met |  | 160 | 160 | 160 | 160 | 160 | 160
Saving Calculation Based on Money Spent on Fuel
| Fuel | Cost ($/Gallon) |  | Money spent On Fuel ($) | Gallons | Efficiency Factor | Useful Output (BTU) | Cost of electricity for heat pump to generate same useful output ($) | Saving ($) |  | Btu per Unit
| Oil-fired tank | 2.3 | Gallon | 1000 | 434.7826 | 0.65 | 39226086.9565 | 229.9302 | 770.0698 |  | 138800 | Gallon
| Propane | 0.67 | Gallon | 1000 | 1492.5373 | 0.65 | 88477611.9403 | 518.6261 | 481.3739 |  | 91200 | Gallon
| Natural Gas | 0.8 | Therm | 1000 | 1250 | 0.65 | 81250000 | 476.2603 | 523.7397 |  | 100000 | Therm
| Resistance Tank | 0.07 | KWH | 1000 | - | 0.9 | 43868571.4286 | 257.1429 | 742.8571 |  | 3412 | KWH
| Enter Electricity Cost | 0.07 | 40: $/kWH; 50: (<----------------------------------ENTER COST OF ELECTRICITY)
Saving Calculation Based on Daily Water Usage
| Fuel Type | Cost ($/Gallon) |  | Hot Water Usage Per day | Annual HW Load (BTU) | Efficiency Factor | Annual Fuel (gallon) | Annual Electricity (kWh) | Annual Cost | Annual Saving | Btu per Unit
| Oil-fired tank | 2.3 | Gallon | 1000 | 167425500 | 0.65 | 1855.7471 |  | 4268.2182 | 2165.2351 | 138800 | Gas/gal
| Propane | 1.7 | Gallon | 1000 | 167425500 | 0.65 | 2824.3168 |  | 4801.3386 | 2698.3554 | 91200 | Propane/gal
| Natural Gas | 1.5 | Therm | 1000 | 167425500 | 0.65 | 2575.7769 |  | 3863.6654 | 1760.6822 | 100000 | Nat Gas/Therm
| Resistance Tank | 0.15 | KWH | 1000 | 167425500 | 0.9 |  | 54521.7859 | 8178.2679 | 6075.2847 | 3412 | Resistance/KWH
| Heat Pump | 0.15 | KWH | 1000 | 167425500 | 3.5 |  | 14019.8878 | 2102.9832 |  | 3412 | KWH
Note on L115: Oil
Note on L116: Propane
Note on L117: Natural Gas
Note on L118: Resistance Heat